{"text_format":"3","workbook":"xlsx","n_sheets":1,"sheets":["预防性试验清单"],"read":"whole","date_system":"1900"}

{"sheet":"预防性试验清单","index":0,"n_rows":115,"n_cols":31,"rows_kept":115,"merged":[[0,0,0,30],[1,0,2,1],[1,2,2,6],[1,7,1,12],[1,13,2,15],[1,16,2,17],[1,18,2,21],[1,22,2,25],[1,26,2,27],[1,28,2,28],[1,29,2,29],[1,30,2,30],[2,7,2,11],[3,0,3,1],[3,2,3,6],[3,7,3,11],[3,13,3,15],[3,16,3,17],[3,18,3,21],[3,22,3,25],[3,26,3,27],[4,0,5,1],[4,2,5,6],[4,7,4,11],[4,13,5,15],[4,16,5,17],[4,18,5,21],[4,22,5,25],[4,26,5,27],[4,28,5,28],[4,29,5,29],[5,7,5,11],[6,0,6,1],[6,2,6,6],[6,7,6,11],[6,13,6,15],[6,16,6,17],[6,18,6,21],[6,22,6,25],[6,26,6,27],[7,0,7,1],[7,2,7,6],[7,7,7,11],[7,13,7,15],[7,16,7,17],[7,18,7,21],[7,22,7,25],[7,26,7,27],[8,0,8,1],[8,2,8,6],[8,7,8,11],[8,13,8,15],[8,16,8,17],[8,18,8,21],[8,22,8,25],[8,26,8,27],[9,0,9,1],[9,2,9,6],[9,7,9,11],[9,13,9,15],[9,16,9,17],[9,18,9,21],[9,22,9,25],[9,26,9,27],[10,0,10,11],[10,13,10,15],[10,16,10,17],[10,18,10,21],[10,22,10,25],[10,26,10,27],[11,0,11,30],[12,0,12,2],[12,3,12,30],[13,1,13,2],[13,3,13,4],[13,5,13,8],[13,9,13,14],[13,16,13,20],[13,21,13,22],[13,23,13,26],[13,27,13,29],[14,0,15,0],[14,1,15,2],[14,3,15,4],[14,5,15,8],[14,9,15,14],[14,16,15,20],[14,21,15,22],[14,23,15,26],[14,27,15,29],[16,1,16,2],[16,3,16,4],[16,5,16,8],[16,9,16,14],[16,16,16,20],[16,21,16,22],[16,23,16,26],[16,27,16,29],[17,1,17,2],[17,3,21,4],[17,5,17,8],[17,9,17,14],[17,15,21,15],[17,16,21,20],[17,21,17,22],[17,23,17,26],[17,27,17,29],[18,1,18,2],[18,5,18,8],[18,9,18,14],[18,21,18,22],[18,23,18,26],[18,27,18,29],[19,1,19,2],[19,5,19,8],[19,9,19,14],[19,21,19,22],[19,23,19,26],[19,27,19,29],[20,1,20,2],[20,5,20,8],[20,9,20,14],[20,21,20,22],[20,23,20,26],[20,27,20,29],[21,1,21,2],[21,5,21,8],[21,9,21,14],[21,21,21,22],[21,23,21,26],[21,27,21,29],[22,1,22,2],[22,3,22,4],[22,5,22,8],[22,9,22,14],[22,16,22,20],[22,21,22,22],[22,23,22,26],[22,27,22,29],[23,1,23,2],[23,3,23,4],[23,5,23,8],[23,9,23,14],[23,16,23,20],[23,21,23,22],[23,23,23,26],[23,27,23,29],[24,1,24,2],[24,3,24,4],[24,5,24,8],[24,9,24,14],[24,16,24,20],[24,21,24,22],[24,23,24,26],[24,27,24,29],[25,1,25,2],[25,3,25,4],[25,5,25,8],[25,9,25,14],[25,16,25,20],[25,21,25,22],[25,23,25,26],[25,27,25,29],[26,1,26,2],[26,3,26,8],[26,9,26,14],[26,16,26,20],[26,21,26,22],[26,23,26,26],[26,27,26,29],[27,0,27,30],[28,0,28,30],[29,0,30,5],[29,6,30,8],[29,9,30,12],[29,13,30,24],[29,25,30,30],[31,0,31,1],[31,2,31,3],[31,4,31,5],[31,6,31,8],[31,9,31,12],[31,13,31,14],[31,15,31,21],[31,22,31,24],[31,25,31,27],[31,28,31,29],[32,0,33,1],[32,2,33,3],[32,4,33,5],[32,6,33,8],[32,9,33,12],[32,13,32,14],[32,15,32,21],[32,22,33,24],[32,25,33,27],[32,28,33,29],[33,13,33,14],[33,15,33,21],[34,0,34,1],[34,2,34,3],[34,4,34,5],[34,6,34,8],[34,9,34,12],[34,13,34,14],[34,15,34,21],[34,22,34,24],[34,25,34,27],[34,28,34,29],[35,0,35,1],[35,2,35,3],[35,4,39,5],[35,6,35,8],[35,9,35,12],[35,13,39,14],[35,15,39,21],[35,22,35,24],[35,25,35,27],[35,28,35,29],[36,0,36,1],[36,2,36,3],[36,6,36,8],[36,9,36,12],[36,22,36,24],[36,25,36,27],[36,28,36,29],[37,0,37,1],[37,2,37,3],[37,6,37,8],[37,9,37,12],[37,22,37,24],[37,25,37,27],[37,28,37,29],[38,0,38,1],[38,2,38,3],[38,6,38,8],[38,9,38,12],[38,22,38,24],[38,25,38,27],[38,28,38,29],[39,0,39,1],[39,2,39,3],[39,6,39,8],[39,9,39,12],[39,22,39,24],[39,25,39,27],[39,28,39,29],[40,0,40,1],[40,2,40,3],[40,4,40,5],[40,6,40,8],[40,9,40,12],[40,13,40,14],[40,15,40,21],[40,22,40,24],[40,25,40,27],[40,28,40,29],[41,0,41,1],[41,2,41,3],[41,4,41,5],[41,6,41,8],[41,9,41,12],[41,13,41,14],[41,15,41,21],[41,22,41,24],[41,25,41,27],[41,28,41,29],[42,0,42,1],[42,2,42,3],[42,4,42,5],[42,6,42,8],[42,9,42,12],[42,13,42,14],[42,15,42,21],[42,22,42,24],[42,25,42,27],[42,28,42,29],[43,0,43,1],[43,2,43,3],[43,4,43,5],[43,6,43,8],[43,9,43,12],[43,13,43,14],[43,15,43,21],[43,22,43,24],[43,25,43,27],[43,28,43,29],[44,0,44,1],[44,2,44,3],[44,4,44,8],[44,9,44,12],[44,13,44,14],[44,15,44,21],[44,22,44,24],[44,25,44,27],[44,28,44,29],[45,0,45,30],[46,0,46,8],[46,9,46,30],[47,0,47,2],[47,3,47,30],[48,0,48,1],[48,2,48,3],[48,4,48,5],[48,6,48,9],[48,10,48,12],[48,13,48,14],[48,15,48,21],[48,22,48,24],[48,25,48,27],[48,28,48,29],[49,0,50,1],[49,2,50,3],[49,4,50,5],[49,6,50,9],[49,10,50,12],[49,13,49,14],[49,15,50,21],[49,22,50,24],[49,25,50,27],[49,28,50,29],[50,13,50,14],[51,0,51,1],[51,2,51,3],[51,4,51,5],[51,6,51,9],[51,10,51,12],[51,13,51,14],[51,15,51,21],[51,22,51,24],[51,25,51,27],[51,28,51,29],[52,0,52,1],[52,2,52,3],[52,4,56,5],[52,6,52,9],[52,10,52,12],[52,13,56,14],[52,15,56,21],[52,22,52,24],[52,25,52,27],[52,28,52,29],[53,0,53,1],[53,2,53,3],[53,6,53,9],[53,10,53,12],[53,22,53,24],[53,25,53,27],[53,28,53,29],[54,0,54,1],[54,2,54,3],[54,6,54,9],[54,10,54,12],[54,22,54,24],[54,25,54,27],[54,28,54,29],[55,0,55,1],[55,2,55,3],[55,6,55,9],[55,10,55,12],[55,22,55,24],[55,25,55,27],[55,28,55,29],[56,0,56,1],[56,2,56,3],[56,6,56,9],[56,10,56,12],[56,22,56,24],[56,25,56,27],[56,28,56,29],[57,0,57,1],[57,2,57,3],[57,4,57,5],[57,6,57,9],[57,10,57,12],[57,13,57,14],[57,15,57,21],[57,22,57,24],[57,25,57,27],[57,28,57,29],[58,0,58,1],[58,2,58,3],[58,4,58,5],[58,6,58,9],[58,10,58,12],[58,13,58,14],[58,15,58,21],[58,22,58,24],[58,25,58,27],[58,28,58,29],[59,0,59,1],[59,2,59,3],[59,4,59,5],[59,6,59,9],[59,10,59,12],[59,13,59,14],[59,15,59,21],[59,22,59,24],[59,25,59,27],[59,28,59,29],[60,0,60,1],[60,2,60,3],[60,4,60,5],[60,6,60,9],[60,10,60,12],[60,13,60,14],[60,15,60,21],[60,22,60,24],[60,25,60,27],[60,28,60,29],[61,0,61,1],[61,2,61,3],[61,4,61,9],[61,10,61,12],[61,13,61,14],[61,15,61,21],[61,22,61,24],[61,25,61,27],[61,28,61,29],[62,0,62,30],[63,0,63,9],[63,10,63,30],[64,0,65,4],[64,5,65,8],[64,9,65,12],[64,13,65,23],[64,24,65,30],[66,1,66,2],[66,3,66,4],[66,5,66,7],[66,8,66,12],[66,13,66,14],[66,15,66,20],[66,21,66,22],[66,23,66,26],[66,27,66,29],[67,0,68,0],[67,1,68,2],[67,3,68,4],[67,5,68,7],[67,8,68,12],[67,13,67,14],[67,15,68,20],[67,21,68,22],[67,23,68,26],[67,27,68,29],[68,13,68,14],[69,1,69,2],[69,3,69,4],[69,5,69,7],[69,8,69,12],[69,13,69,14],[69,15,69,20],[69,21,69,22],[69,23,69,26],[69,27,69,29],[70,1,70,2],[70,3,74,4],[70,5,70,7],[70,8,70,12],[70,13,74,14],[70,15,74,20],[70,21,70,22],[70,23,70,26],[70,27,70,29],[71,1,71,2],[71,5,71,7],[71,8,71,12],[71,21,71,22],[71,23,71,26],[71,27,71,29],[72,1,72,2],[72,5,72,7],[72,8,72,12],[72,21,72,22],[72,23,72,26],[72,27,72,29],[73,1,73,2],[73,5,73,7],[73,8,73,12],[73,21,73,22],[73,23,73,26],[73,27,73,29],[74,1,74,2],[74,5,74,7],[74,8,74,12],[74,21,74,22],[74,23,74,26],[74,27,74,29],[75,1,75,2],[75,3,75,4],[75,5,75,7],[75,8,75,12],[75,13,75,14],[75,15,75,20],[75,21,75,22],[75,23,75,26],[75,27,75,29],[76,1,76,2],[76,3,76,4],[76,5,76,7],[76,8,76,12],[76,13,76,14],[76,15,76,20],[76,21,76,22],[76,23,76,26],[76,27,76,29],[77,1,77,2],[77,3,77,4],[77,5,77,7],[77,8,77,12],[77,13,77,14],[77,15,77,20],[77,21,77,22],[77,23,77,26],[77,27,77,29],[78,1,78,2],[78,3,78,4],[78,5,78,7],[78,8,78,12],[78,13,78,14],[78,15,78,20],[78,21,78,22],[78,23,78,26],[78,27,78,29],[79,1,79,2],[79,3,79,7],[79,8,79,12],[79,13,79,14],[79,15,79,20],[79,21,79,22],[79,23,79,26],[79,27,79,29],[80,0,80,30],[81,0,81,10],[81,11,81,30],[82,0,82,10],[82,11,82,13],[82,14,82,24],[82,25,82,30],[83,1,83,2],[83,3,83,4],[83,5,83,9],[83,10,83,13],[83,15,83,20],[83,21,83,22],[83,23,83,26],[83,27,83,29],[84,0,85,0],[84,1,85,2],[84,3,85,4],[84,5,85,9],[84,10,85,13],[84,15,85,20],[84,21,85,22],[84,23,85,26],[84,27,85,29],[86,1,86,2],[86,3,86,4],[86,5,86,9],[86,10,86,13],[86,15,86,20],[86,21,86,22],[86,23,86,26],[86,27,86,29],[87,1,87,2],[87,3,92,4],[87,5,87,9],[87,10,87,13],[87,14,92,14],[87,15,92,20],[87,21,87,22],[87,23,87,26],[87,27,87,29],[88,1,88,2],[88,5,88,9],[88,10,88,13],[88,21,88,22],[88,23,88,26],[88,27,88,29],[89,1,89,2],[89,5,89,9],[89,10,89,13],[89,21,89,22],[89,23,89,26],[89,27,89,29],[90,1,90,2],[90,5,90,9],[90,10,90,13],[90,21,90,22],[90,23,90,26],[90,27,90,29],[91,1,91,2],[91,5,91,9],[91,10,91,13],[91,21,91,22],[91,23,91,26],[91,27,91,29],[92,1,92,2],[92,5,92,9],[92,10,92,13],[92,21,92,22],[92,23,92,26],[92,27,92,29],[93,1,93,2],[93,3,93,4],[93,5,93,9],[93,10,93,13],[93,15,93,20],[93,21,93,22],[93,23,93,26],[93,27,93,29],[94,1,94,2],[94,3,94,4],[94,5,94,9],[94,10,94,13],[94,15,94,20],[94,21,94,22],[94,23,94,26],[94,27,94,29],[95,1,95,2],[95,3,95,4],[95,5,95,9],[95,10,95,13],[95,15,95,20],[95,21,95,22],[95,23,95,26],[95,27,95,29],[96,1,96,2],[96,3,96,4],[96,5,96,9],[96,10,96,13],[96,15,96,20],[96,21,96,22],[96,23,96,26],[96,27,96,29],[97,1,97,2],[97,3,97,9],[97,10,97,13],[97,15,97,20],[97,21,97,22],[97,23,97,26],[97,27,97,29],[98,0,98,30],[99,0,99,10],[99,11,99,30],[100,0,100,10],[100,11,100,13],[100,14,100,24],[100,25,100,30],[101,1,101,2],[101,3,101,4],[101,5,101,9],[101,10,101,13],[101,15,101,20],[101,21,101,22],[101,23,101,26],[101,27,101,29],[102,0,103,0],[102,1,103,2],[102,3,103,4],[102,5,103,9],[102,10,103,13],[102,15,103,20],[102,21,103,22],[102,23,103,26],[102,27,103,29],[104,1,104,2],[104,3,104,4],[104,5,104,9],[104,10,104,13],[104,15,104,20],[104,21,104,22],[104,23,104,26],[104,27,104,29],[105,1,105,2],[105,3,109,4],[105,5,105,9],[105,10,105,13],[105,14,109,14],[105,15,109,20],[105,21,105,22],[105,23,105,26],[105,27,105,29],[106,1,106,2],[106,5,106,9],[106,10,106,13],[106,21,106,22],[106,23,106,26],[106,27,106,29],[107,1,107,2],[107,5,107,9],[107,10,107,13],[107,21,107,22],[107,23,107,26],[107,27,107,29],[108,1,108,2],[108,5,108,9],[108,10,108,13],[108,21,108,22],[108,23,108,26],[108,27,108,29],[109,1,109,2],[109,5,109,9],[109,10,109,13],[109,21,109,22],[109,23,109,26],[109,27,109,29],[110,1,110,2],[110,3,110,4],[110,5,110,9],[110,10,110,13],[110,15,110,20],[110,21,110,22],[110,23,110,26],[110,27,110,29],[111,1,111,2],[111,3,111,4],[111,5,111,9],[111,10,111,13],[111,15,111,20],[111,21,111,22],[111,23,111,26],[111,27,111,29],[112,1,112,2],[112,3,112,4],[112,5,112,9],[112,10,112,13],[112,15,112,20],[112,21,112,22],[112,23,112,26],[112,27,112,29],[113,1,113,2],[113,3,113,4],[113,5,113,9],[113,10,113,13],[113,15,113,20],[113,21,113,22],[113,23,113,26],[113,27,113,29],[114,1,114,2],[114,3,114,9],[114,10,114,13],[114,15,114,20],[114,21,114,22],[114,23,114,26],[114,27,114,29],[115,0,115,30],[116,0,116,30]]}
["芜湖市建设投资有限公司电房现勘情况"]
["序号","","单位名称","","","","","变压器","","","",null,null,"低压柜\n数量","","","高压柜数量","","母线","","","","电缆","","","","接地网","","继电\n保护","断路\n器","备注"]
[null,"",null,"","","","","规格","","","",null,"数量/台",null,"","",null,"",null,"","","",null,"","","",null,""]
[1,1,"水务局大楼","","","","","400kVA 箱变","","","",null,1,3,3,3,2,2,"10KV1 组","","","","10KV1 根","","","","1 处",""]
[2,2,"皖江金融大厦","","","","","630kVA","","","",null,1,14,14,14,6,6,"10KV1 组","","","","10KV2 根","","","","1 处","",4,4]
[null,"",null,"","","","","800kVA","","","",null,1,null,"","",null,"",null,"","","",null,"","","",null,""]
[3,3,"皖江电子商务中心","","","","","400kVA","","","",null,2,10,10,10,7,7,"10KV1 组","","","","10KV2 根","","","","1 处","",3,3]
[4,4,"九华中路 116 号","","","","","1000kVA","","","",null,1,5,5,5,4,4,"10KV1 组","","","","10KV1 根","","","","1 处","",2,2]
[5,5,"联航大楼","","","","","200kVA","","","",null,1,6,6,6,null,"",null,"","","","10KV2 根","","","","1 处",""]
[6,6,"能源大楼","","","","","160kVA 箱变","","","",null,1,5,5,5,2,2,"10KV1 组","","","","10KV1 根","","","","1 处",""]
["合计","",null,"","","","",null,"","","",null,8,43,43,43,21,21,"5 组","","","","9 根","","","","6 处","",9,9]
["预防性试验清单（水务局造价）",{"$nulls":3},"",null,"",null,"",null,"",{"$nulls":3},"",{"$nulls":5},"",{"$nulls":3},"",""]
[]
["序号","电压\n等级",null,"设备名称","","试验设备","",null,"","检修内容","",{"$nulls":3},"","数量","单位",{"$nulls":4},"检修\n周期",null,"国网执行标准","","",null,"达成效果",null,null,"备注"]
[1,"10kV",null,"电力变压器","","变压器\n1250kva\n1250kva\n2000kva","",null,"","（ 1）测量绕组的直流电阻；\n（ 2）测量绕组连同套管的绝缘电阻、吸\n收比或（和）极化指数；\n（ 3）绕组连同套管的交流耐压试验；\n（4）测温装置及其二次回路试验；","",{"$nulls":3},"",1,"台",{"$nulls":4},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"800kva 以下"]
[{"$nulls":4},"",null,"",null,"",null,"",{"$nulls":3},"",0,{"$nulls":8},"","",{"$nulls":4},"800~2000kva"]
[2,"10kV",null,"电力电缆","","电力电缆","",null,"","(1)测量绝缘电阻；\n(2)非破坏性直流耐压试验及泄漏电流测\n量；","",{"$nulls":3},"",1,"条",{"$nulls":4},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"一次/根"]
[3,"10kV",null,"高压柜",null,"电流/电压互感器","",null,"","(1)测量绕组的绝缘电阻；\n(2)绕组连同套管对外壳的交流耐压试\n验。","",{"$nulls":3},"",2,"台",{"$nulls":4},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"列"]
[4,"10kV",{"$nulls":3},"断路器/负荷开关","",null,"","(1)测量绝缘电阻；\n(2)交流耐压试验（断口、相对地）；\n(3)测量每相导电回路的电阻；\n(4)测量合闸接触器和分、合闸电磁铁线\n圈的绝缘电阻和直流电阻；\n(5)断路器的合闸时间和分分闸时间及相\n间同期限检查；\n(6)最低动作电压测试","",{"$nulls":3},"",{"$nulls":6},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[5,"10kV",{"$nulls":3},"隔离手车","",null,"","(1)测量绝缘电阻；\n(2)交流耐压试验。","",{"$nulls":3},"",{"$nulls":6},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[6,"10kV",{"$nulls":3},"避雷器","",null,"","(1)测量绝缘电阻；\n(2)直流 1mA 电压（U1mA）及 0.75\n（ U1mA）下的泄漏电流测量。","",{"$nulls":3},"",{"$nulls":6},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[7,"10kV",{"$nulls":3},"熔断器","",null,"","测量熔断器的分断能力","",{"$nulls":3},"",{"$nulls":6},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"一组 3 个"]
[8,"10kV",null,"高压母线","","母线","",null,"","（ 1）测量绝缘电阻；\n（ 2）连同套管的交流耐压试验。","",{"$nulls":3},"",1,"组",{"$nulls":4},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"一组"]
[9,"10kV",null,"接地装置","","接地装置","",null,"","测量接地系统的接地电阻。","",{"$nulls":3},"",1,"组",{"$nulls":4},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[10,"10kV",null,"继电保护","","继电保护装置","",null,"","（ 1）保护整定值校核；\n（ 2）整组保护的模拟联跳试验。","",{"$nulls":3},"",0,"台",{"$nulls":4},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[12,"10kV",null,"低压柜","","低压柜","",null,"","(1)绝缘电阻试验\n(2)耐压试验\n(3)整组联动试验","",{"$nulls":3},"",3,"台",{"$nulls":4},"一年",null,"GB/37136-2018","","",null,"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[13,null,null,"清障、清灰","",null,"",null,"","电力设备清灰、现场箱变有树木，春季易燃 ，风险较大，\n需要清理。","",{"$nulls":3},"",1,"处",{"$nulls":4},"一年",null,null,"",""]
[]
["预防性试验清单（皖江金融大厦造价）",{"$nulls":7},"",null,"",{"$nulls":3},"",{"$nulls":5},"",{"$nulls":3},""]
[{"$nulls":14},"",{"$nulls":5},"",{"$nulls":3},""]
[{"$nulls":14},"",{"$nulls":5},"",{"$nulls":3},""]
["号序",null,"电压\n等级",null,"设备名称",null,"试验设备",null,"","检修内容","",null,null,"量数","","位单",{"$nulls":6},"检修\n周期",null,"","国网执行标准",null,null,"达成效果",null,"备注"]
[1,null,"10kV",null,"电力变压器",null,"变压器\n1250kva\n1250kva\n2000kva",null,"","    （ 1）测量绕组的直流电阻；\n    （ 2）测量绕组连同套管的绝\n     缘电阻、吸收比或（和）极化\n     指数；\n    （ 3）绕组连同套管的交流耐\n     压试验；\n    （4）测温装置及其二次回路\n     试验；","",null,null,1,1,"台",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"800kva 以下"]
[{"$nulls":8},"",null,"",null,null,1,1,{"$nulls":9},"",{"$nulls":5},"800~2000kva"]
[2,null,"10kV",null,"电力电缆",null,"电力电缆",null,"","     (1)测量绝缘电阻；\n     (2)非破坏性直流耐压试验及\n     泄漏电流测量；","",null,null,2,2,"条",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"一次/根"]
[3,null,"10kV",null,"高压柜",null,"电流/电压互感\n器",null,"","     (1)测量绕组的绝缘电阻；\n     (2)绕组连同套管对外壳的交\n     流耐压试验。","",null,null,"\n6",null,"台",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"列"]
[4,null,"10kV",{"$nulls":3},"断路器/负荷开\n关",null,"","     (1)测量绝缘电阻；\n     (2)交流耐压试验（断口、相\n     对地）；\n     (3)测量每相导电回路的电\n     阻；\n     (4)测量合闸接触器和分、合\n     闸电磁铁线圈的绝缘电阻和\n     直流电阻；\n     (5)断路器的合闸时间和分分\n     闸时间及相间同期限检查；\n     (6)最低动作电压测试","",{"$nulls":11},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[5,null,"10kV",{"$nulls":3},"隔离手车",null,"","     (1)测量绝缘电阻；\n     (2)交流耐压试验。","",{"$nulls":11},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[6,null,"10kV",{"$nulls":3},"避雷器",null,"","     (1)测量绝缘电阻；\n     (2)直流 1mA 电压（U1mA）\n     及 0.75（ U1mA）下的泄漏\n     电流测量。","",{"$nulls":11},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[7,null,"10kV",{"$nulls":3},"熔断器",null,"","测量熔断器的分断能力","",{"$nulls":11},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"一组 3 个"]
[8,null,"10kV",null,"高压母线",null,"母线",null,"","    （ 1）测量绝缘电阻；\n    （ 2）连同套管的交流耐压试 验。","",null,null,1,1,"组",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"一组"]
[9,null,"10kV",null,"接地装置",null,"接地装置",null,"","测量接地系统的接地电阻。","",null,null,1,1,"组",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[10,null,"10kV",null,"继电保护",null,"继电保护装置",null,"","    （ 1）保护整定值校核；\n    （ 2）整组保护的模拟联跳试\n     验。","",null,null,4,4,"台",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[12,null,"10kV",null,"低压柜",null,"低压柜",null,"","     (1)绝缘电阻试验\n     (2)耐压试验\n     (3)整组联动试验","",null,null,14,14,"台",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[13,{"$nulls":3},"清障、清灰",{"$nulls":3},""," 电力设备清灰、  现场箱变有树木，春季易燃，\n     风险较大 ，需要清理。","",null,null,1,0,"处",{"$nulls":6},"一年",null,""]
[]
[{"$nulls":8},"","预防性试验清单（皖江电子商务中心造价）",{"$nulls":4},"",{"$nulls":9},""]
[{"$nulls":3},"       ",{"$nulls":4},"",{"$nulls":5},"",{"$nulls":9},""]
["序号",null,"电压\n等级",null,"设备名称",null,"试验设备",null,"",null,"检修内容",null,null,"数量","","单位",{"$nulls":6},"检修\n周期",null,"","国网执行标准",null,null,"达成效果",null,"备注"]
[1,null,"10kV",null,"电力变压器",null,"变压器\n1250kva\n1250kva\n2000kva",null,"",null,"（ 1）测量绕组的直流电阻；\n（ 2）测量绕组连同套管的绝\n缘电阻、吸收比或（和）极化\n指数；\n（ 3）绕组连同套管的交流耐\n压试验；\n（4）测温装置及其二次回路\n试验；",null,null,2,2,"台",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"800kva 以下"]
[{"$nulls":8},"",{"$nulls":4},0,0,{"$nulls":9},"",{"$nulls":5},"800~2000kva"]
[2,null,"10kV",null,"电力电缆",null,"电力电缆",null,"",null,"(1)测量绝缘电阻；\n(2)非破坏性直流耐压试验及\n泄漏电流测量；",null,null,2,2,"条",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"一次/根"]
[3,null,"10kV",null,"高压柜",null,"电流/电压互感器",null,"",null,"(1)测量绕组的绝缘电阻；\n(2)绕组连同套管对外壳的交\n流耐压试验。",null,null,7,7,"台",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"列"]
[4,null,"10kV",{"$nulls":3},"断路器/负荷开关",null,"",null,"(1)测量绝缘电阻；\n(2)交流耐压试验（断口、相\n对地）；\n(3)测量每相导电回路的电\n阻；\n(4)测量合闸接触器和分、合\n闸电磁铁线圈的绝缘电阻和\n直流电阻；\n(5)断路器的合闸时间和分分\n闸时间及相间同期限检查；\n(6)最低动作电压测试",{"$nulls":3},"",{"$nulls":7},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[5,null,"10kV",{"$nulls":3},"隔离手车",null,"",null,"(1)测量绝缘电阻；\n(2)交流耐压试验。",{"$nulls":3},"",{"$nulls":7},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[6,null,"10kV",{"$nulls":3},"避雷器",null,"",null,"(1)测量绝缘电阻；\n(2)直流 1mA 电压（U1mA）\n及 0.75（ U1mA）下的泄漏\n电流测量。",{"$nulls":3},"",{"$nulls":7},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[7,null,"10kV",{"$nulls":3},"熔断器",null,"",null,"测量熔断器的分断能力",{"$nulls":3},"",{"$nulls":7},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"一组 3 个"]
[8,null,"10kV",null,"高压母线",null,"母线",null,"",null,"（ 1）测量绝缘电阻；\n（ 2）连同套管的交流耐压试\n验。",null,null,1,1,"组",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度",null,"一组"]
[9,null,"10kV",null,"接地装置",null,"接地装置",null,"",null,"测量接地系统的接地电阻。",null,null,1,1,"组",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[10,null,"10kV",null,"继电保护",null,"继电保护装置",null,"",null,"（ 1）保护整定值校核；\n（ 2）整组保护的模拟联跳试验。",null,null,3,3,"台",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[12,null,"10kV",null,"低压柜",null,"低压柜",null,"",null,"(1)绝缘电阻试验\n(2)耐压试验\n(3)整组联动试验",null,null,10,10,"台",{"$nulls":6},"一年",null,"","GB/37136-2018",null,null,"与初始数据比较对设\n备运行状态，计算老化\n程度"]
[13,{"$nulls":3},"清障、清灰",{"$nulls":3},"",null,"电力设备清灰、现场箱变有树木，春季易燃，\n风险较大 ，需要清理。",null,null,1,0,"处",{"$nulls":6},"一年",null,""]
[]
[{"$nulls":10},"预防性试验清单（九华中路 116 号造价）",{"$nulls":3},""]
[]
[]
["序号","电压\n等级",null,"设备名称",null,"试验设备",null,null,"检修内容",{"$nulls":4},"数量","","单位",{"$nulls":5},"检修\n周期",null,"国网执行标准",{"$nulls":3},"达成效果",null,null,"备注"]
[1,"10kV",null,"电力变压器",null,"变压器\n1250kva\n1250kva\n2000kva",null,null,"（ 1）测量绕组的直流电阻；\n（ 2）测量绕组连同套管的绝缘电\n阻、吸收比或（和）极化指数；\n（ 3）绕组连同套管的交流耐压试\n验；\n（4）测温装置及其二次回路试验；",{"$nulls":4},0,0,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"800kva 以下"]
[{"$nulls":13},1,1,{"$nulls":15},"800~2000kva"]
[2,"10kV",null,"电力电缆",null,"电力电缆",null,null,"(1)测量绝缘电阻；\n(2)非破坏性直流耐压试验及泄漏\n电流测量；",{"$nulls":4},1,1,"条",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"一次/根"]
[3,"10kV",null,"高压柜",null,"电流/电压互\n感器",null,null,"(1)测量绕组的绝缘电阻；\n(2)绕组连同套管对外壳的交流耐\n压试验。",{"$nulls":4},"\n4",null,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"列"]
[4,"10kV",{"$nulls":3},"断路器/负荷\n开关",null,null,"(1)测量绝缘电阻；\n(2)交流耐压试验（断口、相对地）；\n(3)测量每相导电回路的电阻；\n(4)测量合闸接触器和分、合闸电\n磁铁线圈的绝缘电阻和直流电阻；\n(5)断路器的合闸时间和分分闸时\n间及相间同期限检查；\n(6)最低动作电压测试",{"$nulls":12},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[5,"10kV",{"$nulls":3},"隔离手车",null,null,"(1)测量绝缘电阻；\n(2)交流耐压试验。",{"$nulls":12},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[6,"10kV",{"$nulls":3},"避雷器",null,null,"(1)测量绝缘电阻；\n(2)直流 1mA 电压（U1mA）及\n0.75（U1mA）下的泄漏电流测量。",{"$nulls":12},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[7,"10kV",{"$nulls":3},"熔断器",null,null,"测量熔断器的分断能力",{"$nulls":12},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"一组 3 个"]
[8,"10kV",null,"高压母线",null,"母线",null,null,"（ 1）测量绝缘电阻；\n（ 2）连同套管的交流耐压试验。",{"$nulls":4},1,1,"组",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"一组"]
[9,"10kV",null,"接地装置",null,"接地装置",null,null,"测量接地系统的接地电阻。",{"$nulls":4},1,1,"组",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[10,"10kV",null,"继电保护",null,"继电保护装\n置",null,null,"（ 1）保护整定值校核；\n（ 2）整组保护的模拟联跳试验。",{"$nulls":4},2,2,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[12,"10kV",null,"低压柜",null,"低压柜",null,null,"(1)绝缘电阻试验\n(2)耐压试验\n(3)整组联动试验",{"$nulls":4},5,5,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[13,null,null,"清障、清灰",{"$nulls":4},"电力设备清灰、现场箱变有树木，春季易燃，风险\n较大 ，需要清理。",{"$nulls":4},1,0,"处",{"$nulls":5},"一年"]
[]
[{"$nulls":11},"预防性试验清单（联航大楼造价）"]
[]
["序号","电压\n等级",null,"设备名称",null,"试验设备",{"$nulls":4},"检修内容",{"$nulls":3},"数量","单位",{"$nulls":5},"检修\n周期",null,"国网执行标准",{"$nulls":3},"达成效果",null,null,"备注"]
[1,"10kV",null,"电力变压器",null,"变压器\n1250kva\n1250kva\n2000kva",{"$nulls":4},"（ 1）测量绕组的直流电阻；\n（ 2）测量绕组连同套管的绝缘电\n阻、吸收比或（和）极化指数；\n（ 3）绕组连同套管的交流耐压试\n验；\n（4）测温装置及其二次回路试\n验；",{"$nulls":3},1,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"800kva 以下"]
[{"$nulls":14},0,{"$nulls":15},"800~2000kva"]
[2,"10kV",null,"电力电缆",null,"电力电缆",{"$nulls":4},"(1)测量绝缘电阻；\n(2)非破坏性直流耐压试验及泄\n漏电流测量；",{"$nulls":3},2,"条",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"一次/根"]
[3,"10kV",null,"高压柜",null,"电流/电压互感器",{"$nulls":4},"(1)测量绕组的绝缘电阻；\n(2)绕组连同套管对外壳的交流\n耐压试验。",{"$nulls":3},0,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"列"]
[4,"10kV",{"$nulls":3},"断路器/负荷开关",{"$nulls":4},"(1)测量绝缘电阻；\n(2)交流耐压试验（断口、相对\n地）；\n(3)测量每相导电回路的电阻；\n(4)测量合闸接触器和分、合闸电",{"$nulls":10},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[{"$nulls":10},"磁铁线圈的绝缘电阻和直流电\n阻；\n(5)断路器的合闸时间和分分闸\n时间及相间同期限检查；\n(6)最低动作电压测试"]
[5,"10kV",{"$nulls":3},"隔离手车",{"$nulls":4},"(1)测量绝缘电阻；\n(2)交流耐压试验。",{"$nulls":10},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[6,"10kV",{"$nulls":3},"避雷器",{"$nulls":4},"(1)测量绝缘电阻；\n(2)直流 1mA 电压（U1mA）及\n0.75（ U1mA）下的泄漏电流测\n量。",{"$nulls":10},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[7,"10kV",{"$nulls":3},"熔断器",{"$nulls":4},"测量熔断器的分断能力",{"$nulls":10},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"一组 3 个"]
[8,"10kV",null,"高压母线",null,"母线",{"$nulls":4},"（ 1）测量绝缘电阻；\n（ 2）连同套管的交流耐压试验。",{"$nulls":3},0,"组",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度",null,null,"一组"]
[9,"10kV",null,"接地装置",null,"接地装置",{"$nulls":4},"测量接地系统的接地电阻。",{"$nulls":3},1,"组",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[10,"10kV",null,"继电保护",null,"继电保护装置",{"$nulls":4},"（ 1）保护整定值校核；\n（ 2）整组保护的模拟联跳试验。",{"$nulls":3},0,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[12,"10kV",null,"低压柜",null,"低压柜",{"$nulls":4},"(1)绝缘电阻试验\n(2)耐压试验\n(3)整组联动试验",{"$nulls":3},6,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备运\n行状态 ，计算老化程度"]
[13,null,null,"清障、清灰",{"$nulls":6},"电力设备清灰、现场箱变有树木，春季易燃 ，风\n险较大 ，需要清理。",{"$nulls":3},1,"处",{"$nulls":5},"一年"]
[]
[{"$nulls":11},"预防性试验清单（能源大楼造价）"]
[]
["序号","电压\n等级",null,"设备名称",null,"试验设备",{"$nulls":4},"检修内容",{"$nulls":3},"数量","单位",{"$nulls":5},"检修\n周期",null,"国网执行标准",{"$nulls":3},"达成效果",null,null,"备注"]
[1,"10kV",null,"电力变压器",null,"变压器\n1250kva\n1250kva\n2000kva",{"$nulls":4},"（ 1）测量绕组的直流电阻；\n（ 2）测量绕组连同套管的绝缘电\n阻、吸收比或（和）极化指数；\n（ 3）绕组连同套管的交流耐压试\n验；\n（4）测温装置及其二次回路试\n验；",{"$nulls":3},1,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度",null,null,"800kva 以下"]
[{"$nulls":14},0,{"$nulls":15},"800~2000kva"]
[2,"10kV",null,"电力电缆",null,"电力电缆",{"$nulls":4},"(1)测量绝缘电阻；\n(2)非破坏性直流耐压试验及泄\n漏电流测量；",{"$nulls":3},1,"条",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度",null,null,"一次/根"]
[3,"10kV",null,"高压柜",null,"电流/电压互感器",{"$nulls":4},"(1)测量绕组的绝缘电阻；\n(2)绕组连同套管对外壳的交流\n耐压试验。",{"$nulls":3},2,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度",null,null,"列"]
[4,"10kV",{"$nulls":3},"断路器/负荷开关",{"$nulls":4},"(1)测量绝缘电阻；\n(2)交流耐压试验（断口、相对\n地）；\n(3)测量每相导电回路的电阻；\n(4)测量合闸接触器和分、合闸电\n磁铁线圈的绝缘电阻和直流电\n阻；\n(5)断路器的合闸时间和分分闸\n时间及相间同期限检查；\n(6)最低动作电压测试",{"$nulls":10},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度"]
[5,"10kV",{"$nulls":3},"隔离手车",{"$nulls":4},"(1)测量绝缘电阻；\n(2)交流耐压试验。",{"$nulls":10},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度"]
[6,"10kV",{"$nulls":3},"避雷器",{"$nulls":4},"(1)测量绝缘电阻；\n(2)直流 1mA 电压（U1mA）及\n0.75（ U1mA）下的泄漏电流测\n量。",{"$nulls":10},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度"]
[7,"10kV",{"$nulls":3},"熔断器",{"$nulls":4},"测量熔断器的分断能力",{"$nulls":10},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度",null,null,"一组 3 个"]
[8,"10kV",null,"高压母线",null,"母线",{"$nulls":4},"（ 1）测量绝缘电阻；\n（ 2）连同套管的交流耐压试验。",{"$nulls":3},1,"组",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度",null,null,"一组"]
[9,"10kV",null,"接地装置",null,"接地装置",{"$nulls":4},"测量接地系统的接地电阻。",{"$nulls":3},1,"组",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度"]
[10,"10kV",null,"继电保护",null,"继电保护装置",{"$nulls":4},"（ 1）保护整定值校核；\n（ 2）整组保护的模拟联跳试验。",{"$nulls":3},0,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度"]
[12,"10kV",null,"低压柜",null,"低压柜",{"$nulls":4},"(1)绝缘电阻试验\n(2)耐压试验\n(3)整组联动试验",{"$nulls":3},5,"台",{"$nulls":5},"一年",null,"GB/37136-2018",{"$nulls":3},"与初始数据比较对设备\n运行状态 ，计算老化程度"]
[13,null,null,"清障、清灰",{"$nulls":6},"电力设备清灰、现场箱变有树木，春季易燃 ，风\n险较大 ，需要清理。",{"$nulls":3},1,"处",{"$nulls":5},"一年"]